## SCCT Calculator
Calculator for checking the secondary cable length of the CT | [6 empty] | Sec Current | Cable Length | SCCT Type
to see if there is enough burden for the measuring device | [6 empty] | 1 | 0.5 | SCCT-1
[7 empty] | 5 | 3 | SCCT-2
SCCT Current transformer as supplied |  |  | 1 | VA |  |  |  | 5
SCCT Type | SCCT-2
Rated sec. current | 5 | A
Cable length | 0.5 | m |  | SCCT-1 = 5m
Rated output | 1 | VA |  | SCCT-2 (1A) = 3m
Cross section | 1.5 | mm2 |  | SCCT-2 (5A) = 0.5m
Shortening of supplied cable |  |  | 0 | VA
| 0 | m
Cable extension |  |  | 0 | VA
Extension Length | 0 | m
Cross section | 2.5 | mm2 |  |  |  | Typical meter VA:
1A approx 0.01VA
Power consumption of meter |  |  | 0.2 | VA |  | 5A approx 0.2VA
Available output for measurement |  |  | 1 | VA | OK
Instructions :-
1 | Fill in the yellow cells with the appropriate values
2 | The highlighted box will be green if OK, red if cable losses too high.

## Revision History
Revision | Date | Notes
1 | 2012-11-08 | Original version based on manufacturer's calculator
2